1. Device Offline detection:

Current working Method: Usually we will be checking the Heart beat for every 30minutes to know the device is connected with server are in online or offline.

Problem:

Suppose if the device is in offline the Server can detect and confirm the Heart beat for every 30minutes then only in the Mobile app it can show the device is in offline.

The Problem is that mean while if the person try’s to ON/OFF Machine, but the device is in offline so they won’t get any feedback from the Machine, then they cannot know what is happening whether the Machine is offline or online.

Solution:

Whenever the customer refreshes the app, we can take the latest Payload ID from the Event API. After the refresh command is sent to the unit, we can wait around 2 minutes and check the Payload ID again.

* Payload ID changed → Unit responded → Online

* Payload ID unchanged → No response → Offline***

2. Error Update

Current working Method:

| Code | Explanation | Priority |
| --- | --- | --- |
| 1 | Float Switch Fault | HIGH |
| 2 | Power Protection Fault | critical |
| 3 | Indoor Fan Overload protection Fault | HIGH |
| 4 | Indirect Fan Overload protection Fault | HIGH |
| 5 | Indirect Pump Overload protection Fault | HIGH |
| 6 | Filter Clog Fault | LOW |
| 7 | Direct PumpCurrent Missing or Overload | HIGH |
| 8 | Indirect Pump Current Missing or Overload | HIGH |
| 9 | Outdoor Temperature Sensor Error | HIGH |
| 10 | Indirect Temperature Sensor Error | LOW |
| 11 | Air Supply Temperature Sensor Error | LOW |
| 12 | Outdoor Humidity Sensor Error | LOW |
| 13 | Indirect Humidity Sensor Error | LOW |
| 14 | Indoor Temperature Sensor Error | LOW |
| 15 | Indoor Humidity Sensor Error | LOW |
| 16 | Water Level Low at Direct Pump | MEDIUM |
| 17 | Water Level Low at Indirect Pump | MEDIUM |
| 18 | AC Zero Cross Signal Error | LOW |
| 19 | Mother Board and Display Communication Error | LOW |
| 20 | Emergency Shutdown | critical |

Note:

The LOW Priority Errors are should only store in the log and can give error indication but no need to block the On/OFF Functionality’s